## Sheet1
| MASTER SPREADSHEET - facilities built since 2010 | [10 empty] | 2018-08-31 |  | MICKLEY
Reclamation project R16AC00119
FLORIDA FACILIITIES
| BASIC INFORMATION | [10 empty] | ADDITIONAL INFORMATION
[11 empty] | DESAL |  | DESAL DESIGN | DESAL AVERAGE | PLANT DESIGN | PLANT AVERAGE |  | RAW |  | FEED PRESSURE | MEMBRANE | PERMEATE | BLEND |  |  |  | AGE OF MEMBRANE | FATE OF | FATE OF
| COUNTY | NAME | OWNER | CITY | TYPE | PURPOSE | MGD | START | DISPOSAL | WATER | REASON | OF CONCENTRATE | (mgd) | (mgd) | (mgd) | (mgd) | BLENDING? | OR CONDUCTIVITY | PRE-TREATMENT | (psi) | (%) | CONDUCTIVITY | CONDUCTIVITY | (PERMEATE : OTHER) | SOURCE | PERMEATE | (YR) | WASTEWATER | WASTE
[7 empty] | MAX | DESAL | CONCENTRATE | SOURCE | TREATMENT | POST TREATMENT | PRODUCTION | PRODUCTION | PRODUCTION | PRODUCTION |  | WATER TDS |  | TO DESAL | RECOVERY | TDS OR | TDS OR | BLEND RATIO | BLEND WATER | POST-TREATMENT | LAST REPLACEMENT | CLEANING | BACKWASH
| LEE | Green Meadows WTP | Lee County Utilities | Ft. Myers | RO | DW | 7.5 | 2018 | DWI | GW | plant expansion and replacement of old existing facility | none | 7.5 | not on line yet | will vary | not on line yet | yes | 1860 mg/l | sand filter, cartridge filter, acid | 167 | 85 | 36 | 223 | roughly 9 : 6 | bypass and IX treated surficial water | sulfuric acid, degasification, disinfection (chloramination), pH control (caustic), fluoride, corrosion inhibitor | new plant | DWI
| Charlotte & Lee | Babcock Ranch Water System | Babcock Ranch | Babcock Ranch | NF | DW | 0.25 | 2017 | combined with WWTP effluent; used for irrigation | GW | hardness, color | none | 0.25 |  |  |  | yes | 800-950 µS/cm | antiscalant, cartridge filters, sulfuric acid | 108-117 | 84 | 200-250, depends on source wells |  | ~8 : 1 | raw water bypass | blending, degasification, disinfection, caustic, CO2 | had to replace original membranes due to super chlorination incident at start-up
| BROWARD | NSID NF WTP | North Springs Water Improvement District | Coral Springs | NF | DW | 6.75 | 2016 | sewer | GW | taste and odor, TOC, hardness, H2S | [5 empty] | yes |  | strainer, cartridge filter, H2SO4, scale inhibitor |  |  |  |  | 80 to 95 % permeate | source water after cartridge filter | H2SO4, degasification (for H2S), hypochlorite; NaOH of pH stability; corrosion inhibitor; ammonium sulfite to form chloramine to reduce DBP formation
| BROWARD | Coral Springs IMP Dist./DIW++ CSID | Coral Springs Improvement District | Coral Springs | RO | DW | 6.75 | 2016 | DWI (discharge is to tail end of WWTP for DWI) | GW | better water quality | none | 6.75 | ~4 |  |  | yes | 600-700 mg/l | sand strainer, antiscalant, cartridge filters | 93-105 | 85 | 20-45 mg/l | 140 mg/L | 8-15% bypass | bypass after sand strainer and cartridge filters |  | on original membranes | DWI
| PALM BEACH | Hood Road Membrane WP | Seacoast Utilities Authority |  | NF | DW | 26 | 2015 | blend with WWTP effluent for irrigation; when not possible --> DWI | GW | replace lime softening | none | 26 | both an NF and RO plant; varies with demand; at higher demand NF portion is greater; typical = 17.5 | 29.5 (26 MF + 3.5 RO) | varies with demand | no | 800 µS/cm | sand filter, antiscalant, cartridge filter, acid (sulfuric) | 95 | 80 | 350 µS/cm | NAP | NAP | NAP | degasification, disinfection (chloramination), pH adjustment (caustic), corrosion inhibitor (phosphate) | on original membranes | sewer
| PINELLAS | Tarpon Springs RO Facility | City of Tarpon Springs | Tarpon Springs | RO | DW | 6.4 | 2015 | DWI | GW | TDS | none | 6.4 | 2.5 |  |  | yes | 18,000-20,000 µS/cm | acid, antiscalant, cartridge filters | 350 (to 1st stage); 450 (to 2nd stage) | 72 | 297 µS/cm |  | presently only 5 gpm bypass | bypass | pH adjustment (CO2), alkalinity and hardness (lime and caustic), disinfection (hypochlorite), fluoride | on original membranes | DWI (haven't cleaned yet)
| PINELLAS | Clearwater #2 | City of Clearwater | Clearwater | RO | DW | 6.25 | 2015 | DWI | GW | TDS, iron, hardness | none | 6.25 | 2.5 |  |  | yes | 2800-4500 (depends on well mix) | antiscalant, cartridge filters | 180-190 | 80 |  |  |  | surficial aquifer water | ozone (for sulfide removal); chloramination, caustic, stabilization | design flaw led to early scaling with damage to some membranes; still using original membranes on the 1 skid that’s operating | sewer
| PALM BEACH | Hood Road Membrane WP | Seacoast Utilities Authority |  | RO | DW | 3.5 | 2015 | DWI | GW | TDS | none | 3.5 | both an NF and RO plant; varies with demand; at higher demand NF portion is greater; typical = 17.5 | 29.5 (26 MF + 3.5 RO) | varies with demand | no | 6000 µS/cm | antiscalant, cartridge filter, acid (sulfuric) | 240 | 75 | NAV | NAP | NAP | NAP | degassing, disinfection (chloramination), pH adjustment (caustic), corrosion inhibitor (phosphate) | on original membranes | sewer
| HENDRY | Labelle WTP No. 2 | City of Labelle | Labelle | RO | DW | 1.5 | 2014 | DWI | GW | previously out of compliance with THMs; new source water required TDS removal | none | 1.5 | 0.75 | 1.68 |  | yes | depends on which wells are used; 3400 and 4300 µS/cm | antiscalant, pre-filter | 150-160 | 70 | <100 mg/l | 700 µS/cm | ~ 9 : 1 | raw water bypass | degasification, chlorination, fluoridation | on original membranes
| MIAMI-DADE | City of Hialeah RO WTP | City of Hialeah Water and Sewer Department | Hialeah | RO | DW | 7.5 | 2013 | DWI | GW |  | none | 7.5 |  |  |  | no | 5000-5500 µS/cm | acid, antiscalant, cartridge filters | 180-194 | 80 |  |  |  |  | lime, caustic, chlorine | on original membranes | DWI
| BROWARD | Town of Davie WTP/WRF | Town of Davie | Davie | RO | DW | 6 | 2013 | DWI | GW | no new permits for surficial aquifer | none | 6 | 2.6 |  |  | no | 7000-9000 µS/cm | antiscalant, cartridge filters | 230 | 80 | 300-450 mg/l |  |  |  | aeration, disinfection (hypochlorite), fluoride | on original membranes | DWI (haven't cleaned yet)
| BROWARD | West WTP - Deerfield - RO | City of Deerfield Beach | Deerfield | RO | DW | 3 | 2012 | DWI | GW |  | none | 3 |  | 14.5; both an NF and RO plant (11.5 mgd NF built in 2004); |  | yes | 1800-2000 µS/cm | acid, antiscalant, cartridge filter | 186-210 | 78 | NAV | NAV | ~ 3 : 11.5 | NF permeate | orthophosphate, caustic, chlorine | on original membranes | sewer
| PINELLAS | Oldsmar WRF | City of Oldsmar | Oldsmar | RO | DW | 3 | 2012 | DWI | GW |  | none | design = 3; permitted = 2 | 1 | 3.3 | 1.3 | yes | 2800-3500 µS/cm | antiscalant, cartridge filters | 135-145 | 75 | 75-100 mg/l | 75 | 90:10 | conventional WTP product | degasification,, CO2/caustic, chlorine, fluoride, corrosion inhibitor | on original membranes | neutralization, sewer
| ST. LUCIE | Dania Beach | City of Dania Beach | Dania Beach | NF | DW | 2 | 2012 | sewer | GW | iron, hardness |  | 2 | 1 | 5 | 2.2 | yes | 400 mg/l | acid, antiscalant | 42 | 90 | 50-60 | 130-150 | 2:03 | bypass |  | on original membranes
| BROWARD | Springtree | City of Sunrise Utility Complex | Sunrise | RO | DW | 1.5 | 2012 | DWI | GW | TDS | none | 1.5 | in 2017 = 0.389; plant does not operate every day | RO = 15.; lime softening = 24; total = 25.5 | 2017 average = 10.06 | yes | 1605 mg/l | antiscalant, cartridge filters | ~160 | 75 | 55 | 70 | 1.5 : 11 | lime softened water (different aquifer) | degasification, chloramination, fluoridation | on original membranes
| MARTIN | North WTP | South Martin Regional Utility |  | NF | DW | 0.41 | 2012 | sewer | GW | hardness, color |  | 0.41 |  |  |  | yes
| PALM BEACH | City of Lake Worth Lake Worth RO WTP | City of Lake Worth | Lake Worth | RO | DW | 4.5 | 2011 | DWI | GW | TDS; needed new water source | none | 4.5 | 2.7 | 17.4 (4.5 for RO; 12.9 for lime softening) | ~5.5 | yes | 3000-4000 mg/l | antiscalant, acid, cartridge filters | 200 stage 1; 230 stage 2 | 75 |  |  | currently 2.5 : 3.0 | lime softened water | aeration, chloramination | on original membranes
| LEE | North Cape Coral RO WTP | City of Cape Coral Utilities Department | Cape Coral | RO | DW | 12 | 2010 | DWI | GW | TDS | neutralize | 12 |  |  | 8.5 | yes | 2700 mg/l | acid, antiscalant, cartridge filters | 160 | 80 | 100-118 |  | 15-25% bypass | bypass | blend, degasification, chlorine (for disinfection and residual H2S removal, caustic (pH adjustment) | on original membranes | neutralize, DWI
| PUTNAM | East Putnam County RO WTP | Putnam County | East Palatka | RO | DW | 1 | 2010 | surface | GW | needed an alternative water souce |  |  | 0.225 |  |  | yes | 800 mg/l |  |  | 80 | 25 mg/l | 250 mg/l | ~ 2.4 : 1 | bypass |  | 9 years (just replaced)
CALIFORNIA FACILITIES
| BASIC INFORMATION | [10 empty] | ADDITIONAL INFORMATION
[11 empty] | DESAL |  | DESAL DESIGN | DESAL AVERAGE | PLANT DESIGN | PLANT AVERAGE |  | RAW |  | FEED | MEMBRANE | PERMEATE | BLEND |  |  |  | AGE OF MEMBRANE | FATE OF | FATE OF
[7 empty] | MAX | DESAL |  | SOURCE | TREATMENT | POST TREATMENT | PRODUCTION | PRODUCTION | PRODUCTION | PRODUCTION |  | WATER TDS |  | PRESSURE | RECOVERY | TDS OR | TDS OR | BLEND RATIO | BLEND WATER | POST-TREATMENT | LAST REPLACEMENT | CLEANING | BACKWASH
| COUNTY | NAME | OWNER | CITY | TYPE | PURPOSE | MGD | START | DISPOSAL | WATER | REASON | OF CONCENTRATE | (mgd) | (mgd) | (mgd) | (mgd) | BLENDING? | OR CONDUCTIVITY | PRE-TREATMENT | (psi) | (%) | CONDUCTIVITY | CONDUCTIVITY | (PERMEATE : OTHER) | SOURCE | PERMEATE | (YR) | WASTEWATER | WASTE
| LOS ANGELES | Cal Pomona WTP | Cal Pomona Department of Water Operations |  | RO | DW | 0.41 | 2017 | brine lie to LA sanitation | GW | more sustainable water supply | none | 0.41 |  |  |  | yes | 800 mg/l | antiscalant, cartridge filters | 120 | 75 |  |  | ~ 3 : 1 | bypass | pH adjustment, CO2 stripping, chlorine
| SAN BERNARDINO | Wochholz Regional WRF | Yucaipa Valley Water District |  | MF/RO | WRF | 2 | 2017 | some brine line, some recycle | GW | for reuse | none | 2 | 2 | 8 | 4 | yes | depends on wells used | acid, antiscalant, cartridge filters | 80 | 80 | no target | no target | ~ 1 : 1 | bypass after MF | blend, UV
| LOS ANGELES | Signal Hill WTP | City of Signal Hill | Signal Hill | NF | DW | 1.8 | 2017 | sewer | GW | color | none | 1.8 | 0.9 (running 1 of 2 skids) |  |  | no |  | cartridge filters | 77 | 98 |  |  |  |  | none | on original membranes | sewer
| SAN BERNARDINO | Irwin Water Works | Fort Irwin | Fort Irwin | primarily EDR (EDR/MF/RO/evap) | DW | 6 | 2016 | EP | GW | highly variable flow and complexity; nitrate, silica, TDS, F, As | EDR concentrate is lime softened, followed by MF, RO, IX, MVC evaporation | 6 | 1.0-2.0 | 6 | 1.0-2.0 | no | 720 mg/l | chlorination, cartridge filters before EDR; degasification, stripper prior to MF/RO, IX before evaporator |  | 92 (EDR); ~99+ overall | 100 |  |  |  | CO2, lime, chlorine | EDR membrane not replaced; 3rd stage RO replaced after 18 months | evaporation pond | evaporation pond
| SAN DIEGO | Carlsbad Desal Project |  | Carlsbad | SWRO | DW | 50 | 2015 | outfall | ocean | need/demand for DW |  | 54 | 50 | 54 | 50 |  | no | multimedia filter, cartridge filters, microfiltration |  | 50 |  | NA |  |  | stabilization, disinfection (chloramination), carbon dioxide, lime, fluoride | on original membranes
| ORANGE | Aliso Creek WRF | South Coast Water District (SCWD) |  | UF/RO | WRF | 0.65 | 2015 | Coastal Treatment Plant Ocean Outfall | from SCWD Advanced Water Treatment Facility (sand filter, chlorination) via their reservoir) | TDS, nitrate, hardness; for reuse | none | 0.65 | 0.5 |  |  | no | 1100-1500 mg/l | chlorine, UF, cartridge filter, acid, antiscalant | 165-230 | 80 (RO); 85 (UF) | 800 mg/l |  |  |  | decarbonation; then pumped to AWT system to reduce salinity | on original membranes | neutralization, sewer
| VENTURA | Advanced Water Purification Facility | City of Oxnard | Oxnard | MF/RO/AOP | WWTP | 6.25 | 2015 | brine line to Huemene outfall | secondary effluent | for reuse | none | 6.25 | based on demand; high flow avg. = ~4; low flow avg. ~ 1-2 |  |  | no | 2000-3500 µS/cm | cartridge filter, chlorination, MF | 40 | depends on demand; 85% at high flow |  |  |  |  | UV, pH adjustment by decarbonation and lime | on original membranes
| SAN LUIS OBISPO | Cambria Sustainable Water Facility | Cambria Community Services District (CCSD) | Cambria | RO | DW | 0.6 | 2014 | EP | GW | originally for emergency supply; has been offline; may undergo system redesign
| VENTURA | Round Mountain Desalter | Camrosa Water District | Camrosa | RO | DW | 1 | 2014 | brine line to Huemene outfall | GW | TDS, increased water demand, reduces import need | none | 1 | close to 1 |  |  | yes | 1200 mg/l | Fe/Mn oxidation (chlorine), dechlorination, antiscalant, cartridge filters | 125-150 | 75 |  |  | ~ 600 : 85 | bypass | blend, pH adjustment (caustic), chloramination | had membranes replaced under warranty during start-up due to start-up issues | neutralization, sewer
| ORANGE | Wells 21/22 Desalter | Irvine Ranch Water District |  | RO | DW | 1.44 | 2013 | OCSD / HUNTINGTON BEACH OO | GW | nitrate, TDS | none | 1.44 | 0.29 |  |  | yes | 790-820 mg/l | antiscalant, cartridge filters | 145-175 (depends on wells used) | 85 | 300-350 µS/cm |  | currently 77 : 23 | bypass | ph. adjustment (caustic), chloramination | on original membranes | same as concentrate
| ORANGE | Mesa Water Reliability Facility | Mesa Water District | Costa Mesa | NF | DW | 8.6 | 2012 | sewer; some concentrate is recycled | GW | color | antifoam agent | 8.6 |  |  |  | no | 390-460 mg/l | sand filter, antiscalant, cartridge filters |  | 98 |  |  |  |  | pH adjustment, air stripping, pH adjustment again, chloramination | on original membranes | sewer
| SANTA MONICA | Santa Monica Water Treatment Works | City of Santa Monica | Santa Monica | RO | DW | 10 | 2011 | sewer | GW | TDS | none | 10 | 6.9 |  |  | yes | 500 mg/l | greensand filter, GAC, cartridge filters, antiscalant | 90 | 82 | 200 µS/cm | ~ 400 µS/cm | 80 : 20 | bypass after same filtering process | blend, air stripper, caustic, fluoride, chloramination | ~ 6 years | sewer
| ALAMEDA | RARE Richmond Adv. Recycled Expansion | south Coast Water District (SCWD) |  | MF/RO | WWTP | 3.5 | 2010 | goes to Chevron WWTP after primary treatment; final effluent: some to wetlands; some goes to ocean OF to San Pablo Bay | secondary effluent | for reuse | treatment at refinery WWTP | 3.5 | 3.2 |  |  | no | 600-700 mg/l | Amiad filters, MF, cartridge filters | 150-200 | 85 |  |  |  |  | sent to Chevron for reuse in boilers | ~ 5 years | neutralization, sewer
TEXAS FACILITIES
| BASIC INFORMATION | [13 empty] | ADDITIONAL INFORMATION
[11 empty] | DESAL |  | DESAL DESIGN | DESAL AVERAGE | PLANT DESIGN | PLANT AVERAGE |  | RAW |  | FEED | MEMBRANE | PERMEATE | BLEND |  |  |  | AGE OF MEMBRANE | FATE OF | FATE OF
[7 empty] | MAX | DESAL |  | SOURCE | TREATMENT | POST TREATMENT | PRODUCTION | PRODUCTION | PRODUCTION | PRODUCTION |  | WATER TDS |  | PRESSURE | RECOVERY | TDS OR | TDS OR | BLEND RATIO | BLEND WATER | POST-TREATMENT | LAST REPLACEMENT | CLEANING | BACKWASH
| COUNTY | NAME | OWNER | CITY | TYPE | PURPOSE | MGD | START | DISPOSAL | WATER | REASON | OF CONCENTRATE | (mgd) | (mgd) | (mgd) | (mgd) | BLENDING? | OR CONDUCTIVITY | PRE-TREATMENT | (psi) | (%) | CONDUCTIVITY | CONDUCTIVITY | (PERMEATE : OTHER) | SOURCE | PERMEATE | (YR) | WASTEWATER | WASTE
| Hood | City of Granbury WTP | City of Granbury | Granbury | MF/RO | DW | 2.5 | 2017 | surface | surface | bromide | none | 2.5 | 0.7 |  | 0.875 | yes | 1330 µS/cm | MF, cartridge filters, antiscalant | 115-120 | 75 | 30 mg/l | 250 mg/l | 75 : 25 | MF treated bypass | pH adjustment, chloramination | on original membranes | with concentrate
TX | Hidalgo | La Rusias WTP | Military Highway Water Supply Corp. | Los Indios | RO | DW | 1.44 | 2017 | surface
TX |  | City of Abilene - Possum Kingdom Regional Roughing Facility built during draught, then lake filled up, not operating yet | owner ship has not been turned over to City of Abilene | Abilene | RO | WWTP | 1.2 | 2017 | EP and sewer | sewer
TX | Bexar | H2OAKS Center | City of San Antonio | Elmendorf | RO | DW | 10 | 2016 | DWI | GW |  | none | 10 | 7.22 | 12 |  | yes | 1300 mg/l | cartridge filter, pH adjustment, antiscalant |  | 90 | 30-50 | 400 mg/l |  |  | blending, degasification, pH adjustment (sulfuric acid), corrosion control, disinfection, alkalinity adjustment (calcite contactor), stabilization (NaOH)
TX | Wheeler | City of Wheeler TP | City of Wheeler | Wheeler | RO | DW | 0.5 | 2016 | LA (available for watering job locations and roads) | GW | nitrates | none | 0.5 |  |  |  | yes | depends on wells uses; 750-900 µS/cm | antiscalant, cartridge filters | 127-140 | 75 | 15 µS/cm | target based on nitrate level | 2:01 | bypass | chlorine | on original membranes | with concentrate
TX | Gaines | La Tierra RO WTP | BW Primoris | Seminole | RO | DW | 0.65 | 2016 | LA | GW | TDS, arsenic | none | 0.65 | 0.50-0.65 |  |  | yes | 1000-1200 mg/l | acid, antiscalant, cartridge filters | 220-250 | 65-72 | 40-50 mg/l | 250 mg/l | 2 : 1 | bypass | blend, caustic, chlorine | on original membranes | send membranes off site for cleaning
TX |  | Hamby-Abilene | City of Abilene | Abilene | RO | WWTP | 4.2 | 2015 | EP | WWTP | originally to provide IPR source; now used for reuse | none | 4.2 |  | 7 |  | yes | 3200 µS/cm | MBR, ozone, antiscalant, cartridge filter | 127 | 82 | 131 µS/cm |  | ~4.2 : 2.8 | same source, treated by MBR then ozone | blend, chlorination, aeration, dechlorination | on original membranes | neutralization, then recycle to front of process
TX | Haskell | City of Rule WTP | Rule | Rule | RO | DW | 0.086 | 2015 | sewer | GW |  | none | 0.086 | 0.04 |  |  | ; |  | cartridge filter, antiscalant | 120 | 68 |  |  |  |  | blending, disinfection
TX | Cameron | joines Road WTP | Military Highway Water Supply Corp.. | San Benito | RO | DW | 1.44 | 2014 | surface
TX | Parker | Bob Elder WTP | City of Milsap | Milsap | MF/RO | DW |  | 2014 | surface | surface |  | none |  |  |  |  | yes | 1255 ,g/l | MF, cartridge filter, dechlorination, scaling control | 148 | [5 empty] | blending, pH adjustment, disinfection
TX | Howard | Big Spring Water Plant | Colorado River Municipal Water district | Big Spring | MF/RO | ATP (advanced treatment plant) | 2.38 | 2013 | surface | reclaimed water | draught dried up the lake water source; need for a new source for drinking water | none | 2.38 | 1.2 | 2.38 | 1.2 | no | 1845 mg/l | MF, disinfection: UV, pH adjustment, scaling control | 150 | 75 |  |  |  |  | UV oxidation; 5-20% is blended with surface water from one of the reservoirs and then treated again at the Big Spring WTP; the rest goes to an industry | NA
TX |  | City of Roscoe WTP | City of Roscoe | Roscoe | RO | DW | 0.36 | 2013 | sewer | GW | nitrates, hardness | none | 0.36
TX | Hidalgo | Victoria Road RO Plant | North Alamo Supply Corp. | Donna | RO | DW | 2 | 2012 | surface | GW |  |  | 2.25 | 2.25 | 2 | 2 | no | 4000 mg/l | cartridge filter | 150 | 75 | 150 |  |  |  | degasification, pH adjustment, disinfection, anti-corrosion
TX | Hudspeth | Fort Hancock RO Plant 1 | Fort Hancock Water Control & Improvement District | Fort Hancock | RO | DW | 0.43 | 2012 | EP | GW |  | none | 0.43 | 0.04 |  |  | yes |  | cartridge filter | 180 | 78 |  |  |  |  | pH adjustment, disinfection
TX | Knox | City of Benjamin RO WTP | City of Benjamin | Benjamin | RO | DW | 0.072 | 2012 | EP | GW |  |  |  |  | 0.072 | 0.0576 | yes |  | cartridge filter, disinfection: chlorination/chloramination, oxidation | 165 | 71 |  |  |  |  | blending, pH adjustment, antiscalant, disinfection
TX | Hildalgo | Progresso WTP | Military Highway Water Supply Corp. | Progresso | MF/RO | DW | 0.52 | 2011 | surface
TX | Aransas | Aransas Bay Utility WTP | Aransas Bay Utilities Company, LLC |  | RO | DW | 0.2 | 2011 | surface | GW
TX | Stephens | Stephans Regional SUD WTP | Stephens Regional Special Utility District | Breckenridge | RO | DW | 0.4 | 2010 | EP | surface (lake)
TX | Coryell | City of Evant RO WTP | City of Evant | Evant | RO | DW | 0.08 | 2010 | sewer | GW |  | none | 0.08 | 0.065 |  |  | no | 1100 mg/l | cartridge filter, media filter, antiscalant | 190 | 80 | 800
TX | Gaines | 25th and Avenue G | BW Primoris | Seminole | RO | DW | 1.3 | 2016 | LA | GW | TDS, arsenic | none
TX | Parker | Parker County Special Utility District (SUD) WTP |  | Weatherford | RO | DW | 0.4 | 2010 | surface
TX | Gaines | 14th and C | BW Primoris | Seminole | RO | DW | 0.58 | 2016 | LA | GW | TDS, arsenic | none | 0.65 | 0.5-0.65 |  |  | yes | 2500 in summer; rest of year = ~1100 | acid, antiscalant, cartridge filters | 225-250 | 65-70 | 40-50 mg/l | 740 | 2 : 1 | bypass | blend, caustic, chlorine | on original membranes | membranes sent off site for cleaning
| BASIC INFORMATION | [13 empty] | ADDITIONAL INFORMATION
[11 empty] | DESAL |  | DESAL DESIGN | DESAL AVERAGE | PLANT DESIGN | PLANT AVERAGE |  | RAW |  | FEED | MEMBRANE | PERMEATE | BLEND |  |  |  | AGE OF MEMBRANE | FATE OF | FATE OF
[7 empty] | MAX | DESAL |  | SOURCE | TREATMENT | POST TREATMENT | PRODUCTION | PRODUCTION | PRODUCTION | PRODUCTION |  | WATER TDS |  | PRESSURE | RECOVERY | TDS OR | TDS OR | BLEND RATIO | BLEND WATER | POST-TREATMENT | LAST REPLACEMENT | CLEANING | BACKWASH
| COUNTY | NAME | OWNER | CITY | TYPE | PURPOSE | MGD | START | DISPOSAL | WATER | REASON | OF CONCENTRATE | (mgd) | (mgd) | (mgd) | (mgd) | BLENDING? | OR CONDUCTIVITY | PRE-TREATMENT | (psi) | (%) | CONDUCTIVITY | CONDUCTIVITY | (PERMEATE : OTHER) | SOURCE | PERMEATE | (YR) | WASTEWATER | WASTE
NC | Craven | Craven County Potable Water Supply and Treatment Facility | Craven County |  | NF | DW | 3 | 2017 | surface | GW | reduce reliance on Black Creek Aquifer; remove THM and HAA% precursors; TDS, Fe | none | 3 | 1.33; will increase during Spring and Summer |  |  | no | 296 mg/l | antiscalant, cartridge filters | 38-52 | depends on well combo; up to 75% |  |  |  |  | calcite stabilization, chlorination | on original membranes
IA |  | City of Pella WTP | City of Pella | Pella | RO | DW | 3 | 2017 | surface | GW | limited water available in old aquifer, switched to new; required TDS removal | none | 3 | 1.4 | max is 6 mgd (if 3 mgd of lime softening is added in emergency) | 1.8 | yes | 685 mg/l | antiscalant | 101 first stage; 105 second stage | 80 |  | 230 mg/l | 80:20; 20% can vary 10-30% to get desired water quality | bypass | caustic, sodium hypochlorite, fluoride | on original membranes
IA |  | Grimes WTP | City of Grimes | Grimes | RO | DW | 0.8 | 2017 | sewer | GW | better quality | blend with lime softening wastewater | 0.8 |  |  |  | yes | 110 mg/l | bag filter, cartridge filter, antiscalant |  | 85 |  | 80 mg/l | 2 : 1 | lime softened water | blend, chloramination, corrosion inhibitor | on original membranes | haven't had to clean yet
NC |  | SKYCO WTP | Dare County | Manteo | NF | DW | 3 | 2017 | surface | GW | less complicated than IX and membrane found to address bromide removal and iron | none | 3 | 3 | 5 | 2.5 | yes | 545 mg/l | antiscalant, 5µ cartridge filter | 108 | 80 | 50 | 170 | 3:2 | product water from IX facility; adds back hardness | caustic, hypochlorite, corrosion inhibitor | on original membranes | with concentrate | with concentrate
KS |  | PWWSD #26 | City of Strong City | Strong City | RO | DW | 0.46 | 2015 | surface | GW | hardness | none | 0.46 | 0.12 (currently run 1 of 2 skids; run both skids in summer) | 0.6 | 0.14 | yes | 820-915 µS/cm | chlorination, greensand filter, dechlorination, antiscalant, cartridge filters | 150 | 80 | 15 mg/l | 200 mg/l | 80 : 20 | bypass after greensand filter | caustic, chlorine | on original membranes | sewer; (clean only once every 3 years) | settling tank, solids to lagoon and evaporation pond; retentate back to front of process
KS |  | Big Springs WTP | Douglas County RWD #3 | Tecumseh | RO | DW | 1.14 | 2014 | surface | GW | hardness | none |  | 0.31 |  | 0.67 |  | 280 mg/l |  | 146
OH |  | Spencerville WTP | City of Spencerville | Spencerville | NF | DW | 0.48692 | 2014 | sewer | GW | TDS (from residential IX discharges); ability to meet future concerns | neutralization | 0.49 |  |  |  | yes |  | aeration, chlorination, sand filters, dechlorination, antiscalant | 122 | 70 | 74 mg/l |  |  | sand filtered bypass | disinfection, pH adjustment | on original membranes
CO |  | Sterling WTF | City of Sterling | Sterling | RO | DW | 9.6 | 2013 | DWI/sewer | GW | TDS, uranium, hardness | 25 µ filter, antiscalant | 9.6 | 4 |  |  | yes | 700-1900 µS/cm | antiscalant, cartridge filters | 112-130 | 82 |  |  | 80 : 20 | same wells except for one that goes directly to RO; filtered to 1 µ | bioscrub to remove odor, stabilization, disinfection, pH adjustment
MA |  | Swansea Desalination Treatment Facility | City of Swansea | Swansea | MF/RO | DW | 1.2 | 2013 | surface - to River during high tide events | surface |  |  | 1.2 | 0.4 | 2.18 | 0.85 | yes |  | intake screen, cuastic, coagulant, strainers, mmicfrofiltration | 250-550 depending on feed conductivity | 30-50 depending on feed conductivity |  | 250 mg/l | 40 : 60 | groundwater |  | on original membranes |  | through sand lined lagoon then mixed with concentrate
NJ |  | Glassboro | City of Glassboro | Glassboro | RO/VSEP | DW | 1.13 | 2012 | sewer | GW | TDS | none | 1.13 |  | ~1.5 | ~1 | yes |  | 1µ cartridge filters | ~ 200 |  |  |  | ~ 1:1 | bypass after filters | chlorine, orthophosphate | on original membranes
CO |  | Northern WTP | ECCV Water & Sanitation District | East Cherry Creek | RO | DW | 7 | 2012 | DWI | GW | TDS, hardness | none | 7 | 6.5 | 11 | 7.7 | yes | 900-1100 mg/l | antiscalant, 5 µ cartridge filter | 140-170 | 75 |  | 250-300 mg/l | 70:30 | UV treated bypass | disinfection (hypochlorite), pH adjustment (caustic) | low pressure membrane are original; one replacement on one high pressure skid
ND |  | Emmons County WTP | South Central W District | Linton | UF/RO | DW | 1.2 | 2012 | surface (lake) | surface (lake) | hardness | none | 1.2 | 0.4 | 2 | 0.7 | yes | 500 mg/l | ozone, coagulation, sedimentation, UF, antiscalant | 120 | 80 | 30 mg/l | 250 mg/l | 60 : 40 | bypass | blend, ozone, chlorine | 6 years | with concentrate
OH |  | City of Bowling Green | City of Bowling Green | Bowling Green | RO | DW | 3 | 2012 | surface | surface | THM, TOC | none | 3 | 1 | 14 | 4.8 | yes | 650 µS/cm | antiscalant cartridge filters, microfiltration | 75 | 78 | 16 µS/cm |  | 25 : 75 | lime softened/GAC treated water | blend, pH adjustment, chlorination | on original membranes | with concentrate
IL |  | Brimfield WP | City of Brimfield | Brimfield | RO | DW | 0.25 | 2012 | sewer | GW | TDS, organics radionuclides | none | 0.25
MI |  | Allegan WTP | City of Allegan | Allegan | RO | DW | 2.25 | 2011 | surface | GW | hardness, LS too complicated and labor intensive | none | 2.25 | ~1.2; about 0.9 in winter and 1.5 in summer |  |  | yes | 700 µS/cm | spiral wound filter, antiscalant | 150 |  |  |  | 70 : 30 | bypass (treated for iron removal) | fluoride, chlorine, orthophosphate | on original membranes | have not cleaned yet
GA |  | Kings Bay Naval Base WTP | King Bay Naval Base | Kings Bay | NF | DW | 2.0003 | 2011 | sewer | [9 empty] | acid, antiscalant
IA |  | Atkins WTP | City of Atkins | Atkins | RO | DW | 0.58 | 2010 | sewer | GW | NH3; so system can grow in future | none | 0.58 |  |  |  | no | 820 µS/cm | 25µ filter, 1µ woven filter; antiscalant | [6 empty] | CaCl2, NaHCO3, caustic, chlorine, orthophosphate
CO |  | Arapahoe County ACWWA WPP | Arapahoe County Water and WW Authority | Centennial | RO | DW | 9 | 2010 | surface | GW | [6 empty] | yes | [7 empty] | MF permeate
IA |  | Hartley | City of Hartley | Hartley | RO | DW | 0.44 | 2010 | sewer | GW | hardness, SO4, TDS | none | 0.44 | summer = 0.17; winter = 0.11 |  |  | yes | 2100 mg/l | antiscalant, cartridge filters | 158 | 75-77 |  | 400 mg/l | 90 : 10 | bypass | aeration, chlorine, caustic, corrosion inhibitor, fluoride | on original membranes | sewer
NC |  | New Frontier Way NF WTP | City of Jacksonville | Jacksonville | NF | DW | 8 | 2010 | surface | GW | hardness, organics | none | 8 | 3.5 |  |  | yes | 884 | antiscalant, cartridge filters | 57 | 75 | 75 | 280-320 | 90:10 | bypass | bioscrubbing to remove odor, stabilization, disinfection, pH adjustment
OH |  | City of Delaware WTP | City of Delaware | Delaware | UF/NF and NF (separate systems) | DW | 6 |  | surface | surface and GW | Fe, Mn |  | 6 | 3.8 |  |  | no |  | on surface water: coagulation, settling, UF; on GW: pressure filters to remove Fe, Mn, | [6 empty] | chorine, corrosion inhibitor, fluoride
IA |  | Hills Water Supply | Hills Municipal Water | Hills | RO | DW | 0.317 | 2015 | sewer | GW | perchlorate, NH3, TDS, hardness | none | 0.317 |  |  |  | no
IA |  | Council Point Water Purification Plant | Council Bluffs Water Works | Council Bluffs | RO | DW | 5 | 2013 | surface | GW | TDS, organics | none | 5 | 1.68 | 5 | 2.4 | yes | 550-800 mg/l | Fe and Mn oxidation, UF, antiscalant | 150 | 75 | Target is potable water hardness | Target is potable water hardness; TDS = 300-400 | 70:30 | bypass | disinfection, pH adjustment | 3 years
UT |  | Southwest GW Treatment Plant | Jordan Valley Water Conservation District |  | RO | DW | 8.25 | 2012 | surface (to Great Salt Lake) | GW | SO4, TDS | none | 8.25; currently limited to 5.5 | 4 | 7.5 | 5.5 | yes | 800 mg/l | antiscalant, cartridge filters | 130 -190 | 80 |  | 225 mg/l | 4 : 1.5 | bypass after 1µ cartridge filter | caustic, disinfection | lead elements replaced after ~ 5 years | sewer
TN |  | Pigeon Forge new STP | City of Pigeon Forge | Pigeon Forge | NF | WWTP | 0.4 | 2015 | NF used for thickening between digesters | sewage after initial digester |  |  | 0.4 |  |  |  | n0 | [8 empty] | disk filter, chlorine, dechlorination, (later this year will recycle to front of process due to high P content) | on original membranes
ND |  | Valley City WTP | Valley City | Valley City | UF/NF | DW | 4.6536 | 2012 | surface (unless low flow in which case it goes to a lagoon) | surface and GW | SO4, hardness | none | 4.65 |  |  |  | yes |  | permanganate (for Fe/Mn), coagulant, acid, UF, antiscalant, cartridge filters | 180 | 85 | 50 µS/cm |  | ~ 1 : 1 | bypass after UF | blend, caustic, chloramination, fluoride | on original membranes | with concentrate
NC |  | Dixon WTP | ONWASA (Onslow Water and Sewer Authority) | Holly Ridge | RO | DW | 3 | 2013 | surface | GW | silica and TOC | none | 3 | 2 | 4 | 2.5 | yes | 400 µS/cm | greensand filter, antiscalant, cartridge filters | 82-98 | 70-80 | 25 | <250 | 73:27 | bypass after greensand filter | pH adjustment (caustic), disinfection, corrosion inhibitor, fluoride | on original membranes | with concentrate
NJ |  | Freese Street WTP | Keansburg Water Department | Keansburg | RO | DW | 1.15 | 2011 | surface | GW | Fe, TDS | none | 1.15 | 0.85 |  |  | yes | 1200-1300 mg/l | antiscalant, acid, cartridge filters | 180-200 | 85 | 40 mg/l |  | 4 : 1 | bypass | caustic, chlorine |  | with concentrate
NC |  | Englehard | Hyde County Water Maintenance and Solid Waste Department | Englehard | RO | DW | 0.432 | 2011 | surface | GW | organics | none | 0.432 |  |  |  | no | 973 µS/cm | antiscalant |  |  | ~25 |  |  |  | acid, lime, phosphate, chlorine | on original membranes
KS |  | Clay Center WTP | City of Clay Center | Clay Center | RO | DW | 1.67 | 2010 | surface | GW | meets present and future needs | none | 1.67 | 0.41 | 1.95 | 0.49 | yes | 1430 µS/cm | greensand filter, antiscalant, cartridge filter |  | 75 |  |  | ~ 80 : 20 | bypass | decarbonation, caustic, chlorine | on original membranes
ND |  | City of Hillsboro WTP | City of Hillsboro | Hillsboro | RO | DW | 0.85 | 2012 |  | GW | hardness, SO4, TDS
NC |  | Tyrrell County Prison RO WTP | Tyrrell County Prison |  | RO | DW | 0.432 | 2010 | surface | GW